## Cover Sheet
ROOM DATA SHEET FORMAT - Cover Sheet October 2021
Room Data Sheets shall be created during Programming/ Schematic Design to communicate the building user’s requirements for each room/space type or by each room in the project. The Architect/Engineer shall work with the building users to develop the Room Data Sheets using the U-M Room Data Sheet template. The U-M Room Data Sheet template is not all-inclusive but is meant to act as a baseline for Room Data Sheet information. Please include project specific and additional items as needed. Room Data Sheets are to be updated periodically as the project progresses and shall be submitted for Owner’s Review at each project phase as part of the Owner's Project Requirements (OPR) and Basis of Design (BOD). Room Data Sheets are to be completed by DD phase and the mechanical sections indicated are to be updated, as needed, during CD phasethrough As-Builts.Information included in the Room Data Sheets is meant to complement the OPR/BOD document without being repetitive. This Cover Sheet shall be updated to include additional abbreviations as required by the project. Include the Cover Sheet as the first page of the Room Data Sheet section in the OPR/BOD document. Each room/space type shall have a sketch accompanied with the Room Data Sheet. At a minimum, the sketch shall include equipment, casework and accessories locations as well as electrical voltage needed. Also, include room dimensions and a brief description of how the room will be used. To ensure that each room will meet the building user's needs reviewers are strongly encouraged to review the Room Data Sheet information carefully, and distribute to other building users that may need to review the documents.
| Abbreviations |  | NFPA | National Fire Protection Association
| ACH | Air Changes Per Hour | NC | Noise Coefficient
| A | Amps | N/A | Non Applicable
| CUH | Cabinet Unit Heater | PT | Paint
| CB | Chilled Beam | Ph | Phase
| CV | Constant Volume | POS | Point of Sale
| EMI | Electromagnetic Interference | PSI | Pounds per Square Inch
| F | Fahrenheit | Pwr. | Power
| FCU | Fan Coil Unit | RADPANEL | Radiant Panel
| FC | Footcandles | RADFLR | Radiant Floor
| FTR | Fin Tube Radiation | RADWALL | Radiant Wall
| GPM | Gallons per Minute | RH | Relative Humidity
| Gen. | General | RO | Reverse Osmosis
| HPUMP | Heat Pump | RODI | Reverse Osmosis Deionized
| In. HG | Inch of Mercury | RB | Rubber Base
| In. w.c. | Inch of Water | STC | Sound Transmission Class
| LMVR | Laboratory Minimum Ventilation Rate | W/SF | Watts per Square Foot
| LVT | Luxury Vinyl Tile | W | Wire
| Max | Maximum | UH | Unit Heater
| Min | Minimum | VV | Variable Volume
| MR-ACT | Moisture Resistant Acoustical Ceiling Tile | V | Volts
| MR-GYP | Moisture Resistant Gypsum Board | VRF-FCU | Variable Refrigerant Flow Fan Coil Unit

## Room Data 1
Check Box if Revised
Classroom |  |  |  | 100, 101, 102
Program Space Name |  |  |  | Room Number(s)
LSA / Biology |  |  |  | DD/ 01-10-2021
Department |  |  |  | Design Phase / Date
Include Sketch of Room At a minimum, sketch to include the following: - Room Dimensions (Height-Width-Depth) - Room Square Footage - Equipment Locations (with callout to indicate outlet requirement) - Accessory Locations - Wiring Devices (receptacles, data outlets, switches, etc)
Architectural Requirements |  |  |  | Equipment (Include quantity and list heat output V/A/Ph)*:
Wall Finish | GYP/ PT | Floor Finish | LVT | Fume Hoods | 2 | FH-01, 02
Base Finish | RB | Ceiling Finish | ACT | Biosafety Cabinets |  | BSC-1
Daylight | Clerestory | Daylight Control | Blackout Shade | Snorkels
Security | Card Access | Signage Types | Room / Rules | Freezers
Direct Adjacencies |  | Offices |  | Other Equipment
Indirect Adjacencies |  | Vivarium
Non-Adjacencies |  | Substation
Structural Impact |  | Tier seating
Hazardous Materials |  | N/A
Maximum Code Occupancy |  | 50
Maximum Design Occupancy |  | 50
Accessories (Include amount and description)
Tele-Data System Requirements
Tele/ Data Outlet Boxes (list size and location)
|  |  |  | Workstations | 2 Gang/ 1 per every 2 workstations
Room Use |  |  |  | Conference Table | Single Gang/ Floor box
Copier - Printer
AV PC
Other (e.g. POS, Vending, etc.)
Notes: * Include additional sheets for equipment if required |  |  |  | Wireless Access | Y | Number of Wireless Users |  | 10
|  |  |  | Wireless Applications | Video Streaming, Email, Texting

## Room Data 2
Classroom | [8 empty] | Electrical Requirements
Program Space Name | [8 empty] | 120V, 20A (See sketch for location, function & equipment tag)
[9 empty] | General Purpose/ Duplex | Duplex Gen. Purpose |  |  | 4 | Workstation Quadplex |  |  |  | 2
Department | [8 empty] | Dedicated Duplex |  |  |  | 2 | Standby Duplex |  |  |  | 2
100, 101, 102 | [8 empty] | 208V Receptacle (See sketch for location, function & equipment tag)
Room Number(s) | [8 empty] | Quantity |  | 1 | Amps, Wire, Phase |  |  | 20A, 3 Wire, Single Phase | 20A, 3 Wire, Single Phase
DD/ 10-10-2010 | [8 empty] | Special Power
Design Phase / Date | [8 empty] | UPS - Loads Served |  |  |  | Workstations
Auxiliary System Requirements | [8 empty] | Normal Pwr |  | Y | Nameplate Voltage |  |  | 208V | Phase |  | 1Ph
AV System | [8 empty] | Standby Pwr |  | N | Amperage |  |  | 5.8A | Wire |  | 3W
Multimedia |  |  | Local PC, Blue Ray | [5 empty] | Connection Type |  |  | Cord and Plug, NEMA configuration L6-15
Sound Reinforcement |  |  | Ceiling Speakers | [5 empty] | Lighting Requirements
Interfaces |  |  | Lighting, Shade Controls, Fire Alarm | [5 empty] | Worksurface Foot Candles |  |  |  | 50 | Type |  |  | LED
Tele Conferencing |  |  | Y | Video Conferencing |  |  |  | N | ON/OFF Control |  | Vacancy sensor/control switch at entrance |  | Vacancy sensor/control switch at entrance
Connections to UM-TV |  |  | N | Connections to Cable TV |  |  |  | N | Zone Control |  |  | Single |  | Ltg Level Control |  |  | Single
Flat Panel Display |  |  | Y | Projector |  |  |  | N | Task Lighting |  |  | Under cabinet at work stations w/ local control
Intercom System |  |  | N | Room Scheduling System |  |  |  | N | Daylighting Control |  |  |  | Y | Method |  | Integral w/ light fixture
Clock System |  |  | N | Assistive Listening System |  |  |  | Y | Standby Power |  |  |  | Y | Function |  | Illuminate work bench
Plumbing / Process Requirements | [8 empty] | Egress Lighting |  |  |  | Y | Interface with AV System (Y/N) |  |  |  | N
Potable Water - Sink Type 1 |  |  | 1 | Cold: |  | Y | Hot: | Y | The following sections shall be updated through AS-BUILTS
|  |  |  | RO: |  |  | RODI: | Y | Mechanical Requirements
Potable Water - Sink Type 2 |  |  | 1 | Cold: |  | Y | Hot: | Y | HVAC
|  |  |  | RO: |  |  | RODI: | Y | Temperature Range °F (1,2) |  |  |  |  | Humidity Range %RH (1,3)
Potable Water - Sink Type x |  |  | N/A | Cold: | Cold: |  | Hot: |  | Ventilation
|  |  |  | RO: | RO: |  | RODI: |  | LMVR Applies |  |  |  | Y | Once Through Air |  |  |  | Y
Hose Bib |  |  | N/A | Cold: | Cold: |  | Hot: |  | Occupied ACH |  |  |  | 6 | Unoccupied ACH |  |  |  | 4
Eye Wash |  |  | 1 | Type: | Cold: |  |  |  | Pressurization +/- ˜ (4) |  |  |  |  | Max HVAC-Noise (NC)
|  |  |  | Location |  |  |  |  | HVAC Control (5)
Shower |  |  | 1 | Type: |  |  |  |  | Heat Gain (Watts or W/SF)
|  |  |  | Location: |  |  |  |  | Lighting (W/SF): |  |  |  |  | Equipment (6):
High Purity Water | [8 empty] | Special HVAC Requirements:
RO | x | RODI: |  | Local Polisher
Waste Systems
Sanitary Drain: |  |  |  | Floor Drain: |  |  |  |  | Process Cooling
Acid Waste Drain: |  |  |  | Floor Sink: |  |  |  |  | Temperature °F |  |  |  |  | Flow Rate (GPM)
Sink: |  |  |  | Trench Drain: |  |  |  |  | Pressure Drop (PSI)
Cup Sink: | [8 empty] | Exhaust:
Central Gas/ Vacuum Systems | [8 empty] | See equipment section for exhaust requirements
Vacuum (In. HG) |  |  |  | Natural Gas (In. w.c.)
Compressed Air (PSI) | [8 empty] | Notes: (1) If special T or H requirements are provided, they are described under “Special HVAC Requirements,” otherwise T & H will be provided as indicated. (2) Temperature will be maintained within the stated range year round. Temperature set point is adjustable including outside the range, but is not guaranteed to be achievable year round. (3) Humidity will be maintained within the stated range year round. Humidity setpoint is not adjustable. (4) +/-/~ = positive, negative, or neutral respectively. (5) Zone or Room HVAC Concept, e.g. VV, CV, FCU, CB, FTR, etc. (list all that apply). (6) Equipment by name and corresponding wattage or list W/SF).
Specialty Gas/ Other (list w/ pressure)
Local Systems (List additional systems)
CO2 |  |  |  | Auto Change Over (Y/N)
Vacuum
Plumbing Notes: